## Slide 1: Water: The Natural Choice
For Efficiency
  Unit efficiency versus Building System efficiency
  Equipment Ratings
    EER and COP
    SEER
    IEER vs IPLV
      IEER is an integrated performance for a central chiller
      Validity is possible because of diversity
      All chillers would use the same raring points and conditions
      IEER loses validity for unitary equipment when equipment is variable but load is not!

## Slide 2: Unit Efficiency – Sustainable for life
EER is simple
  Output of unit in BTU divided by input power
  Every unit, a chiller, a rooftop, unitary equipment
  that uses refrigerant has an EER
    Energy Efficiency Ratio
    EER is BTU per hour output in cooling/power input
    Example a one ton unit delivers 12,000 Btuh/1000 watts for fan and compressor = 12 EER

## Slide 3: Unit Efficiency (be careful) – Not a building
Why SEER and IEER?
  Adjusted performance to show potential blended rating
  Adjusted to include part load operation over a specific range of outdoor air temperatures
  Because outdoor air temperature affects both capacity and efficiency of an outdoor condensing unit.
    SEER – Seasonally adjusted used primarily for residential equipment
    IEER – Integrated to include both seasonal and part load per formula
Problems
  How to apply adjusted ratings to actual building
  Operation of equipment outside ratings

## Slide 4: SEER – why – Residential is more comparable
Applied residentially based on the fact that the majority of residential units are installed very similar. Actual varies by size, location and weather, but all are tested to the same weather so they can be compared to each other.
  A condenser outside
  An air hander inside
  And a refrigerant line set between them
    Pre-charged with refrigerant
    Factory-sealed
    Purchased from wholesaler or unit manufacturer

## Slide 5: SEER – a test for comparison
All manufacturers of residential split units form a committee at AHRI – Air Conditioning, Heating, and Refrigeration Institute
Those manufactures agree to apply a Specific Seasonal adjustment to their equipment EER.
  All members test to an agreed performance with matching Condenser, Air handler, and line set containing refrigerant
  A package tested to a fixed set of conditions

## Slide 6: SEER
SEER is like the MPG sticker on your car.
  It is not what you will expect to get
  It is a comparison of manufacturers of like models
  To a prescribed set of conditions
SEER is the same type of process of comparison
It does not work commercially and is not used
  Too many Variables

## Slide 7: What’s wrong with SEER? Fixed refrigerant lines and fixed weather conditions
Commercially – you need a professional because:
  The buildings are all different
  The installations have many variations
  The occupancy and use of the building are not “typical”
  Energy Efficiency Ratio (EER) that can be modeled
    EER is the unit output versus power consumed at a specific point as a base
      Not what you expect in the building - a common comparison point
      Water is tested at design operating condition – air is not
      And all Manufacturers use EER at the same conditions

## Slide 8: What is IEER?
Another way to compare performance of equipment among manufacturers of identical equipment in a lab
It is:
  Like Equipment to Like equipment – not building systems
  Like units are tested at the same conditions per a lab’s capability
  The prescriptive conditions are NOT how your building operates
IEER should be applied to a total building not a unit.
IEER is not valid for units with static loads (especially when occupied
during the heat of the day).
A building has a system – a condensing unit is not a system

## Slide 9: Key point Certified vs Actual
IEER and the test is created by the MEMBER manufacturers
The test results are monitored by AHRI
AHRI does not create the test points
AHRI verifies that the member company’s test to the standard the Manufacturers created.
  The standard test has to be reproducible in a laboratory
  NOT your building! Location (Weather) or Operation
  Split units cannot perform “as tested” because they are not shipped or installed “as tested” or operate “as tested”

## Slide 10: IEER – Based on unit capacity not load
Adjusted Performance average
  IEER = (0.020 * A) + (0.617 * B) + (0.238 * C) + (0.125 * D) Where: Both air delivered and outdoor air temperature are reduced (02.0%)A = EER at 100% net capacity at AHRI standard rating conditions (95⁰F) (61.7%)B = EER at 75% net capacity and reduced ambient (81.5⁰F for air-cooled) (23.8%)C = EER at 50% net capacity and reduced ambient (68⁰F for air-cooled) (12.5%)D = EER at 25% net capacity and reduced ambient (65⁰F for air-cooled)
  Split DX - with only 25 feet of refrigerant tubing – FLAT – no lift
  Room is always 80 degrees increasing equipment capacity as measured by the Laboratory; there is no part load if 80 in the space!

## Slide 11: Problem with IEER – when is a 12 a 21?
Actual screen shot from AHRI directory
EER is the unit power consumption vs output at one point
IEER is adjusted
Not to your building – to a test
Confusing?
Misleading?
Yes, Benchmarking is the friend of Hydronic Systems because they
deliver at the utility bill.

## Slide 12: Hydronic Advantages
With Water the system operates inside design parameters
The lowest cost way to transport energy
Hydronic systems maintain efficiency
You choose air delivery or radiant delivery
Water-cooled units are more efficient because of
high heat transfer capability
Terminal units receive controlled Design water temperatures
It is water – it can be variable flow and temperature

## Slide 13: High Heat Transfer? Cooling a hot skillet - What is Faster?
Water
even
100 degree dishwater
Wave around in
70 degree air

## Slide 14: Protect your investment in Efficiency
Water always Wins
Equipment and components exceed 20 years
Options and Choice fit the budget
Options and Choice meet Owner Requirements
Options and Choice ensure system life
Options and Choice ensure system integration for the whole building – Forward and Backward compatible
For the Life of YOUR BUILDING

## Slide 15: Water: The Natural Choice
www.hia-c.org